## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: General Manager-KSCC General Manager Ernakulam
Work Name:GENERAL-Construction of Homeopathy Hospital-Electrification-General Electrical Work
Contract No: #######
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Estimate | [7 empty] | 1 | [45 empty] | H | 2397523478 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.001 | OD34059/2023-2024:Supply and wiring points according to IS 732-1989 using rigid PVC medium conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.50 sq mm green coloured FRLS PVC insulated stranded single core copper conductor cable 650V grade, required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories).Single Control light point with 6A, plate ceiling rose - Short point | BI01010001010000000000000515BI0100001114 | 31 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23444494830 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.002 | OD34060/2023-2024:Supply and wiring points according to IS 732-1989 using rigid PVC medium conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.50 sq mm green coloured FRLS PVC insulated stranded single core copper conductor cable 650V grade, required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories). Single control light point without ceiling rose - Short point | BI01010001010000000000000515BI0100001115 | 17 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23132494849 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.003 | OD34061/2023-2024:Supply and wiring points according to IS 732-1989 using rigid PVC medium conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.50 sq mm green coloured FRLS PVC insulated stranded single core copper conductor cable 650V grade,required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories).Single control ceiling fan point with 6 A, 3 plate ceiling rose & with socket size stepped electronic regulator. - Short point | BI01010001010000000000000515BI0100001116 | 11 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23625494850 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.004 | OD34062/2023-2024:Supply and wiring points according to IS 732-1989 using rigid medium gauge PVC conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.50 sq mm green coloured FRLS PVC insulated stranded single core copper conductor cable 650V grade, required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories). Call bell point with 6 A bell push at one end and 6 A, 3 plate ceiling rose at other end - Short point | BI01010001010000000000000515BI0100001117 | 2 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23406494836 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.005 | OD34063/2023-2024:Supply and wiring points according to IS 732-1989 using rigid PVC medium conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.50 sq mm green coloured FRLS PVC insulated stranded single core copper conductor cable 650V grade, required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories). Combined plug point with 6 A, 5 pin plug socket controlled by 6 A, switch in the same switch board as that of light points | BI01010001010000000000000515BI0100001118 | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23803494845 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.006 | OD34064/2023-2024:Supply and wiring points according to IS 732-1989 using rigid PVC medium gauge conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988,cutting the walls, fixing the conduit concealed suitably and with 1.50 sq mm FRLS PVC insulated stranded single core copper conductor cable 650V grade, including providing switch board main and continuous earthing with 1.5 sqmm green coloured FRLS PVC insulated stranded single core copper conductor ,required quantity of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (RoHS compliant modular accessories). Independent plug - Short point | BI01010001010000000000000515BI0100001119 | 2 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23499494843 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.007 | 1.21.1:Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm | BI01010001010000000000000515BI0100001120 | 100 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23528494855 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.008 | 1.21.2:Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.25 mm | BI01010001010000000000000515BI0100001121 | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23778494856 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.009 | 1.27.1:Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.1 or 2 Module (75mmX75mm) | BI01010001010000000000000515BI0100001122 | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23425494864 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.01 | 1.27.2:Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.3 Module (100mmX75mm) | BI01010001010000000000000515BI0100001123 | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23400494865 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.011 | 1.27.4:Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.6 Module (200mmX75mm) | BI01010001010000000000000515BI0100001124 | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23288494866 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.012 | 1.17.3:Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 X 1.5 sq.mm | BI01010001010000000000000515BI0100001125 | 100 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23126494853 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.013 | 1.17.12:Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 2.5 sq. mm | BI01010001010000000000000515BI0100001126 | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23176494852 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.014 | 1.18.2:Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor,unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.2 Pair | BI01010001010000000000000515BI0100001127 | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23626494854 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.015 | 1.24.1:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.5/6 amps switch | BI01010001010000000000000515BI0100001128 | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23728494857 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.016 | 1.24.3:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.15/16 amp switch | BI01010001010000000000000515BI0100001129 | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23941494858 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.017 | 1.24.4:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.3 pin 5/6 amp socket outlet | BI01010001010000000000000515BI0100001130 | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23578494859 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.018 | 1.24.5:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.6 pin 15/16 amp socket outlet | BI01010001010000000000000515BI0100001131 | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23512494860 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.019 | 1.24.6:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.Telephone socket outlet | BI01010001010000000000000515BI0100001132 | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23838494861 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 1.24.7:Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.TV antenna socket outlet | BI01010001010000000000000515BI0100001133 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23843494862 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.021 | 1.26:Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | BI01010001010000000000000515BI0100001134 | 12 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23534494863 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.022 | 90.5.1.3:Supply and fixing the following types of superior quality 250V A.C call bell on existing M.S. box and giving connections with required length of 3 core, 16 / 0.20mm 650/1100V grade PVC insulated and PVC sheathed round copper conductor flex wire conforming to relevant ISS or with the extended original wiring, earthing the MS box and making good the surface as required.Ding dong bell | BI01010001010000000000000515BI0100001135 | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23165494886 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.023 | 90.3.21.3:Supply & installation of light fittings on 'C/U' shaped flat iron bracket Supply, conveyance, installation, testing and commissioning the light fittings of following types made from 0.5mm CRCA sheet complete with all accessories and lamps etc. directly on wall using 2 nos. 'C/U' brackets made from 20 x 3 mm MS flat, painting the flat iron bracket and giving connections with required length of 16/0.20mm 3 core copper conductor flex wire conforming to relevant ISS or extending the original wiring and giving connection etc. as required.1200 mm 1X20W LED Lamp with box type fixture | BI01010001010000000000000515BI0100001136 | 19 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23704494883 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.024 | 90.3.18.2:Supply, fabrication, conveyance and fixing the following sizes of B class GI pipe bent to shape / cut and welded to shape and fixing the same to wall / parapet using clamps as noted along with each size, painting with 2 coats of synthetic enamel paint over a coat of zinc chromate primer, making good the damages, colour washing etc as required.32 mm dia with HG company fabricated clamps | BI01010001010000000000000515BI0100001137 | 2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23193494882 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.025 | 90.15.4.1:Supply Conveyance, installation, testing and commissioning of 20W LED street light output greater than 105lumen/W 4000-6000 K with IP 66 protection LED Chip make Cree/Lumilled/Nichea with power factor greater than 0.95 at full load, internal surge protection up to 8 KV,and Aluminium pressure die-cast Powder coated housing,acrylic cover complete with THD Less than10%, power factor greater than 0.98, RoHS compliant, duly wired up for use on 230 V AC supply. Driver compartment should be seperatly accessible for maintenance (LM 79&80 certificates from NABL accredited Third party lab to be produced mentioning chip manufacturer) | BI01010001010000000000000515BI0100001138 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23905494877 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.026 | OD34065/2023-2024:Supply and fixing low glare high efficiency square surface mounted LED flat panel 230V 50Hz Compton make LCDSPLN-S-18-CDL 18 w light fitting complete with all required accessories etc. as required | BI01010001010000000000000515BI0100001139 | 11 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23128494841 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.027 | OD34066/2023-2024:Supply and installation of compact modern design utility bulkhead with energy savings Crompton STUD type 10W LED fitting | BI01010001010000000000000515BI0100001140 | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23169494828 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.028 | OD34067/2023-2024:Supplying and fixing PVC batten/ angle holder with PVC shade, 9W LED bulb and giving connection etc. as required. | BI01010001010000000000000515BI0100001141 | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23701494829 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.029 | 90.4.1:Supply and installation of suitable size MS rod type fan clamp in the RCC slab as per IS 732 as required. | BI01010001010000000000000515BI0100001142 | 11 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23143494881 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | 90.4.5.4:Supply, Installation, testing and commissioning of ceiling fan of following sizes including wiring the down rods of standard length (up to 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. 1200mm sweep - ceiling fan complete with service value minimum 4.0(cub meter/minute/Watt), Air delivery minimum 210(cubic meter/minute), Copper winding suitable for 230V/240V single phase AC supply | BI01010001010000000000000515BI0100001143 | 11 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23126494884 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.031 | 90.4.8:Charges for cutting holes suitable for accommodating exhaust fans up to 305mm sweep including plastering colour washing etc. as required. | BI01010001010000000000000515BI0100001144 | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23461494885 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.032 | OD34068/2023-2024:Supply, conveyance, installation, testing and commissioning of 225mm light duty exhaust fan in metal frame in the existing opening, fixing necessary bolt and nuts, making good the damages etc. as required including giving connections with required length of 24/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS. | BI01010001010000000000000515BI0100001145 | 6 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23891494835 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.033 | 90.11.1.12:Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required8 way (8+24) - three phase double cover (IP 42/43) | BI01010001010000000000000515BI0100001146 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23751494875 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.034 | 2.10.1:Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Single pole | BI01010001010000000000000515BI0100001147 | 13 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23116494867 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.035 | 2.10.4:Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Triple pole | BI01010001010000000000000515BI0100001148 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23750494868 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.036 | 2.11:Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | BI01010001010000000000000515BI0100001149 | 12 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23820494869 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.037 | 2.13.2:Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.63 amps | BI01010001010000000000000515BI0100001150 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23802494871 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.038 | 2.15.3:Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.63 amps | BI01010001010000000000000515BI0100001151 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23337494872 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.039 | 2.17:Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | BI01010001010000000000000515BI0100001152 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23993494873 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | 90.12.7.41:Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required.4 core 16 sq mm with factory made clamp | BI01010001010000000000000515BI0100001153 | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23399494876 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.041 | 90.16.1.3:Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required3.15 mm copper conductor ( 10 SWG) | BI01010001010000000000000515BI0100001154 | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23143494878 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.042 | 9.1.33:Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 16 sq. mm (28mm) | BI01010001010000000000000515BI0100001155 | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23498494887 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.043 | OD34069/2023-2024:Supplying and providing earth clamps for siemens/ tripodular type cable glands of suitable length and other dimensions noted along with each size of glands for 4sqmm-16 sq mm sizes of cables with 12 mm wide x 1 mm thick clip as required. | BI01010001010000000000000515BI0100001156 | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23322494846 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.044 | 5.4:Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | BI01010001010000000000000515BI0100001157 | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23954494874 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.045 | OD34070/2023-2024:Supply and laying bare earthing conductors of size3.15 mm copper conductor (10 SWG) laid 0.6 m below ground level including excavating trench of suitable size and refilling etc. as required (in ordinary soil). | BI01010001010000000000000515BI0100001158 | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23418494838 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.046 | OD34071/2023-2024:Supply and providing 25 x 3 mm GI strip earth lead from the test joint to the earth electrode using the following sizes of conductors/ strips including cutting, drilling necessary holes (in case of strip) and fixing firmly with plate test joint etc as required. | BI01010001010000000000000515BI0100001159 | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23909494839 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.047 | OD34072/2023-2024: Supply and providing test joint for the earthing system using 2 Nos of 2x25x3mm of GI strip including cutting and bending to shape, drilling necessary holes and fixed to the watering pipe etc as required. | BI01010001010000000000000515BI0100001160 | 0.6 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23676494840 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.048 | 90.16.2.2:Supply and laying of the following sizes of B class GI pipe laid 0.6 m below ground level including excavating trench of suitable size and refilling etc, as required.20 mm dia. G.I pipe ( medium class) | BI01010001010000000000000515BI0100001161 | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23354494879 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.049 | 90.16.5.3:Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required.3.15 mm (10 SWG) | BI01010001010000000000000515BI0100001162 | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23609494880 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.05 | OD34073/2023-2024:Supply and providing 25 x 3 mm brass bolt & nut with washers on the existing MS box / earth bus etc. as required including drilling necessary holes as required | BI01010001010000000000000515BI0100001163 | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23258494831 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.051 | OD34074/2023-2024:Supply and providing 12 x 3 mm brass bolt & nut with washers on the existing MS box / earth bus etc. as required including drilling necessary holes as required | BI01010001010000000000000515BI0100001164 | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23449494844 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.052 | 2.1.2:Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.63 Amp TP & N | BI01010001010000000000000515BI0100001165 | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23801494870 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.053 | OD34075/2023-2024: Fabricating and fixing enclosure for 63 Amps TP&N dis-connector fuse switch unit with handle assembly and HRC fuse as required. | BI01010001010000000000000515BI0100001166 | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23168494832 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.054 | OD34076/2023-2024:Supply and Installation / Fixing / Provision of Outdoor type size 600X300x214 mm HENSEL make K 0400 with hinged lid, plain side wall and meter fixing rail suitable to fix Single Phase / Three Phase Energy Meter in suitable base plate and having a provision for Fuse / MCB cutout with complete tamper proof SEALING facility. | BI01010001010000000000000515BI0100001167 | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23525494842 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.055 | OD34077/2023-2024:63 A, 415 V, DIN type fuse base | BI01010001010000000000000515BI0100001168 | 3 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23730494833 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.056 | OD34078/2023-2024:Supply and fixing 63 A, 415 V, 2 way neutral link mounted on DMC/ SMC base | BI01010001010000000000000515BI0100001169 | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23339494848 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.057 | OD34079/2023-2024:Supply and fixing 2 -80A, DIN type fuse link of size in the existing meter board and giving connections etc. | BI01010001010000000000000515BI0100001170 | 3 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23392494837 | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.058 | OD34080/2023-2024:Supply and clamping the following sizes of "B" class GI pipe on wall with all required accessories & clamps etc., including cutting and making good the walls, painting the exposed portions etc., as protective covering to earth leads / cables/service entry pipe | BI01010001010000000000000515BI0100001171 | 2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23108494847 | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.059 | OD34081/2023-2024:Supply and providing iron hook for binding KSEB service wire. | BI01010001010000000000000515BI0100001172 | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23931494834 | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.06 | OD34082/2023-2024:Painting letters or figures of size 2.50 cm, 4 cm or 5 cm height with enamel paint as identification mark to SB, DB, panel board etc as required | BI01010001010000000000000515BI0100001173 | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | S | 23415494851 | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information